## FEBRUARY 2026
Parameter | Tag | Unit | PG TEST DATA | Set 4 - Base Load | Set 3 - Base Load | Set 2 - Base Load | Set 1 - Base Load
Date |  |  | 2025-01-27 | 2025-12-23 | 2025-04-20 | 2024-12-22 | 2024-09-13
Time |  |  | 17:52 | 16:21 | 23:14 | 2:31 | 8:09
GT LOAD | DWATT | MW | 236 | 239 | 234.94 | 249.79 | 241.5
REACTIVE POWER | DVAR | MVAR | 65 | 64 | -11 | -24 | 48
IGV | CSGV | % | 87.96 | 87.9 | 87.8 | 87.9 | 87.8
IBH | CSBHX | % | 7.24 | 0 | 0 | 0 | 0
AMBIENT PRESSURE | AFPIP | MMHG | 674 | 674 | 676 | 675 | 676
AMBIENT TEMPERATURE | ATID | DEGC | 30.4 | 25.2 | 25 | 20.6 | 33.4
COMPRESSOR INLET AIR FLOW | AFQ | KG/SEC | 563.6 | 550.6 | 539.8 | NA | NA
COMPRESSOR INLET PRESSURE | AFPCS | MMWC | 46.65 | 53.36 | 51.16 | 47.97 | 45.78
COMPRESSOR INLET TEMPERATURE | CTIM | DEGC | 30.4 | 25.3 | 25.2 | 22.4 | 23.8
COMPRESSOR DISCAHRGE PRESSURE | CPD | KG/CM2 | 14.69 | 14.8 | 14.6 | 15.2 | 15
COMPRESSOR DISCAHRGE TEMPERATURE | CTD | DEGC | 436.8 | 431.5 | 427.4 | 426.2 | 424.5
REFERENCE SPEED | TNR | RPM | 103.6 | 105.45 | 105.3 | 103.81 | 103.77
ACTUAL SPEED | TNH | RPM | 2997.4 | 2996.98 | 2984.45 | 2998.73 | 3003.22
FSR |  | % | 79.57 | 85.51 | 85.1 | 87.46 | 86.23
SRV |  | % | 51.81 | 50.47 | 49.98 | 55.89 | 50.32
CA-CRT |  | % | 102.37 | 101.9 | 101.8 | 102.7 | 100.8
EXHAUST TEMPERATURE | TTXM | DEGC | 656.96 | 655.8 | 657.2 | 656.9 | 643.7
MAXIMUM EXHAUST TEMPERATURE | TTXD#1/31 | DEGC | 681.1 | 677 | 673 | 676 | 666
EXHAUST FLOW | EXHMASS | KG/SEC | 552.14 | 565.16 | 550.47 | 575.15 | 572.45
FUEL GAS FLOW | FQG | KG/SEC | 10.32 | 12.52 | 10.32 | 10.81 | 10.75
FUEL GAS PRESSURE | FPG#1 (P1) | KG/CM2 | 31.85 | 33.7 | 33.7 | 31.4 | 34.2
FUEL GAS TEMPERATURE | FTG | DEGC | 173.4 | 175.3 | 176.6 | 170.4 | 171.4
FUEL GAS PRESSURE | FPG#2(P2) | KG/CM2 | 26 | 25.9 | 25.9 | 26 | 26
D5 (REF) | VGC#1 | % | -25 | -25 | 28.7 | -25 | -25
D5 (ACTUAL) |  | % | 0.1 | 0.1 | 28.7 | 0.1 | 0.2
PM1(REF) | VGC#2 | % | 29.5 | 30.2 | 30.3 | 30.3 | 36.1
PM1(ACTUAL) |  | % | 29.5 | 29.3 | 30.3 | 30.2 | 36.1
PM2(REF) | VGC#3 | % | 55.2 | 58 | 57.5 | 57.1 | 56.6
PM2(ACTUAL) |  | % | 55.2 | 57.7 | 57.5 | 57.1 | 56.6
PM3(REF) | VGC#4 | % | 56.5 | 54 | 30.6 | 58.4 | 53.9
PM3(ACTUAL) |  | % | 56.5 | 54 | 30.6 | 58.4 | 54
MODE |  |  | 6.3 | 6.3 | 6D | 6.3 | 6.3
FLAME INTENSITY-1 | 1 | % | 81 | 81.4 | 88.7 | 80.8 | 91.2
FLAME INTENSITY-2 | 2 | % | 82 | 80.1 | 94.3 | 83.4 | 94.4
FLAME INTENSITY-3 | 3 | % | 79 | 77.2 | 93.1 | 79.9 | 89.5
FLAME INTENSITY-4 | 4 | % | 77 | 75.5 | 92.7 | 76.9 | 87.4
MAX TURBINE COMPARTMENT TEMPERATURE-1 | ATTC1A | DEGC | 116 | 118.2 | 113.9 | 104.7 | 119.9
MAX TURBINE COMPARTMENT TEMPERATURE-2 | ATTC1B | DEGC | 107 | 113.59 | 108.8 | 99.6 | 129.1
MAX TURBINE COMPARTMENT TEMPERATURE-3 | ATTC1C | DEGC | 113 | 129.57 | 113.9 | 101.6 | 130.3
MAX TURBINE COMPARTMENT TEMPERATURE-4 | ATTC2B | DEGC | 113 | 117.61 | 109.2 | 103.9 | 111.7
MAX TURBINE COMPARTMENT TEMPERATURE-5 | ATTC2C | DEGC | 114 | 110 | 119.2 | 105.7 | 98.5
MAX TURBINE COMPARTMENT TEMPERATURE-6 | ATTC4 | DEGC | 116 | 100.3 | 94.6 | 88.4 | 139.3
MAX TURBINE COMPARTMENT TEMPERATURE-7 | ATT2A | DEGC | 98 | 117.61 | 109.2 | 100.9 | 123.2
MAX TURBINE COMPARTMENT TEMPERATURE-8 | ATTC5 | DEGC | 106 | 111 | 99.4 | 92.7 | 126.4
SPREAD#1 | TTXSP#1 | DEGC | 30.77 | 28 | 32.09 | 35.61 | 30.11
SPREAD#2 | TTXSP#2 | DEGC | 25.84 | 21.58 | 24.95 | 29.2 | 25.74
SPREAD#3 | TTXSP#3 | DEGC | 24.77 | 21.47 | NA | NA | 23.63
SPREAD#4 | TTXSP#4 | DEGC | 20.67 | 17.96 | NA | NA | 22.81
ALLOWABLE SPREAD | TTXSPL | DEGC | 78.13 | 78.39 | NA | NA | 77.22
CPR RATIO (CAL) |  |  | 17.17 | NA | 17.52 | NA | NA
CPR RATIO (ACT) |  |  | 17.02 | 17.21 | 17.025 | NA | 17.337
IBH EXHAUST MASS FLOW | CQBH | KG/SEC | 0 | 0 | 0 | 0 | 0
SEISMIC VIBRATION Bearing 1 X Axis | 39V-1A | MM/SEC | 5.49 | 5.8 | 4.61 | 7.07 | 6.1
SEISMIC VIBRATION Bearing 1 Y Axis | 39V-1B | MM/SEC | 5.31 | 5.42 | 4.31 | 6.68 | 6.16
SEISMIC VIBRATION Bearing 2 X Axis | 39V- 2A | MM/SEC | 2.85 | 2.63 | 2.58 | 3.19 | 3.02
SEISMIC VIBRATION Bearing 2 Y Axis | 39V- 2B | MM/SEC | 3.07 | 2.78 | 2.69 | 3.19 | 3.12
SEISMIC VIBRATION Bearing 3 X Axis | 39V- 5A | MM/SEC | 5.11 | 5.05 | 3.94 | 5.54 | 5.23
SEISMIC VIBRATION Bearing 3 Y Axis | 39V- 5B | MM/SEC | 5.34 | 5.26 | 3.99 | 5.47 | 5.14
SEISMIC VIBRATION Bearing 4 X Axis | 39V- 6A | MM/SEC | 5.53 | 4.78 | 3.64 | 6.23 | 2.94
SEISMIC VIBRATION Bearing 4 Y Axis | 39V- 6B | MM/SEC | 5.42 | 4.7 | 3.62 | 6.11 | 2.87
SEISMIC VIBRATION Bearing 5 X Axis | 39V- 8A | MM/SEC | 1.44 | 1.27 | 1.24 | 1.15 | 0.85
SEISMIC VIBRATION Bearing 5 Y Axis | 39V- 8B | MM/SEC | 3.07 | 2.47 | 3.56 | 3.17 | 3.02
1st Stage Wheel Space Temperature ( Forward Inner Top) | TTWS1FI1 | DEGC | 509.8 | 511.3 | 505 | 498.7 | 506.9
1st Stage Wheel Space Temperature ( Forward Inner Bottom) | TTWS1FI2 | DEGC | 512.2 | 513.1 | 505 | 499.4 | 509.5
1st Stage Wheel Space Temperature ( After Outer Top) | TTWS1AO1 | DEGC | 492.1 | 489.6 | 487 | 476.4 | 489.4
1st Stage Wheel Space Temperature ( After Outer Bottom) | TTWS1AO2 | DEGC | 510.1 | 510.1 | 513 | 499.9 | 507.6
2nd Stage Wheel Space Temperature ( Forward Outer Top) | TTWS2FO1 | DEGC | 504.3 | 509 | 513 | 505.3 | 505.2
2nd Stage Wheel Space Temperature ( Forward Outer Bottom) | TTWS2FO2 | DEGC | 507.3 | 511.8 | 516 | 508.6 | 508
2nd Stage Wheel Space Temperature ( After Outer Top) | TTWS2AO1 | DEGC | 431.8 | 430.1 | 427 | 422.6 | 430.5
2nd Stage Wheel Space Temperature ( After Outer Bottom) | TTWS2AO2 | DEGC | 327.8 | 358.6 | 336 | 289.9 | 295.8
3rd Stage Wheel Space Temperature ( Forward Outer Top) | TTWS3FO1 | DEGC | 317.4 | 320.4 | 323 | 314 | 311.2
3rd Stage Wheel Space Temperature ( Forward Outer Bottom) | TTWS3FO2 | DEGC | 458.5 | 453.3 | 446 | 441.8 | 464.8
3rd Stage Wheel Space Temperature ( After Outer Top) | TTWS3AO1 | DEGC | 346.9 | 333.2 | 325 | 317.3 | 343.5
3rd Stage Wheel Space Temperature ( After Outer Bottom) | TTWS3AO2 | DEGC | 348.5 | 334.3 | 325 | 318.8 | 344.7
Bearing 1 Bottom Max Temperature | BTJ1_1 | DEGC | 96.57 | 94.3 | 100.5 | 93 | 106.6
Bearing 1 Top Max Temperature | BTJ1_2 | DEGC | 102.64 | 101.6 | 107.7 | 98.3 | 115.6
Beaing 2 Bottom Max Temperature | BTJ2_1 | DEGC | 93.58 | 92.8 | 92.5 | 94.2 | 90.5
Beaing 2 Top Max Temperature | BTJ2_2 | DEGC | 90.95 | 91.3 | 91.1 | 91.6 | 90.6
Bearing 4 Temperature | LTG1D | DEGC | 45.41 | 59.6 | 44.9 | 41.6 | 42
Bearing 3 Temperature | LTG2D | DEGC | 67.43 | 68 | 69.4 | 66.6 | 69.2
THRUST BEARING TMPERATURE ACTIVE MAX | BT-T11 | DEGC | 80.3 | 80 | 81.3 | 79.1 | 81.6
THRUST BEARING TMPERATURE IN ACTIVE MAX | BT-TA1 | DEGC | 80 | 79.8 | 80 | 89 | 90.9
MAX DRAIN OIL TEMPERATURE |  | DEGC | 67.3 | 74.3 | 76.1 | 73.2 | 76.2
EXTRATION FLOW FROM 9TH&13TH STAGE |  | KG/SEC | 5.44 | 5.47/7.84 | 5.29/6.65 | 5.55 | 5.16/7.04
EXTRATION FLOW FROM 9TH&13TH STAGE |  | KG/SEC | 8 | 5.36/7.79 | 5.3/6.68 | 7.97 | 4.57/7.03
LUBE OIL HEADER PRESSURE |  | KG/CM2 | 2.09 | 2 | 2 | 2 | 2
LUBE OIL HEADER TEMPERATURE |  | DEGC | 57.51 | 57.4 | 59.1 | 56.2 | 59.2
LUBE OIL TANK VACUUM |  | MMWC | 229.29 | 222.29 | 262.4 | 233.9 | 234.56
HYDRAULIC OIL PRESSURE |  | KG/CM2 | 113.89 | 114.3 | 113.16 | 113.7 | 113.6
MAX EXHAUST PRESSURE | 96EP#1/2#3 | MMWC | 184.3 | 192.8 | 175.7 | 196.6 | 189.95
MAX TURBINE BEARING TUNNEL TEMP | TTIB#1/2&3 | DEGC | 128 | 153.26 | 143.1 | 127.7 | 124.3
INLET AIR DIFFERENTIAL PRESSURE DATA | 96TF#1/2A/2B | MMWC | 22.88 | 30.78 | 27.79 | 17.78 | 22.31

## Sheet1
27.01.2025
17:52
PF
GENERATOR VOLTAGE
FREQUENCY
GENERATOR CURRENTS
EXCITATION VOLTAGE
EXCITATION CURRENTS
AMBIENT TEMPERATURE
COMPRESSOR INLET AIR FLOW
FUEL GAS PRESSURE
IBH EXHAUST MASS FLOW
MAX SESIMIC VIBRATION
H2 CASING PRESSURE
H2 PURITY
SEAL OIL DISCHARGE PRESSURE
SEAL OIL TANK VACCUM
COLD .GAS INLET WATER TEMP (CH#1/2)
HOT GAS TEMP (CH#1/2)
COLD GAS TCV
GEN STATOR WINDING TEMP
GEN STATOR CORE TEMP(T.E)
GEN STATOR CORE TEMP(E.E)
MAX GEN BEARING TEMP